## Disclaimer
The National Laboratory of the Rockies (NLR) is operated for the U.S. Department of Energy (DOE) by the Alliance for Energy Innovation, LLC ("Alliance").
Access to or use of any data or software made available on this server ("Data") shall impose the following obligations on the user, and use of the Data constitutes user's agreement to these terms. The user is granted the right, without any fee or cost, to use or copy the Data, provided that this entire notice appears in all copies of the Data. Further, the user agrees to credit DOE/NLR/ALLIANCE in any publication that results from the use of the Data. The names DOE/NLR/ALLIANCE, however, may not be used in any advertising or publicity to endorse or promote any products or commercial entities unless specific written permission is obtained from DOE/NLR/ ALLIANCE. The user also understands that DOE/NLR/ALLIANCE are not obligated to provide the user with any support, consulting, training or assistance of any kind with regard to the use of the Data or to provide the user with any updates, revisions or new versions thereof. DOE, NLR, and ALLIANCE do not guarantee or endorse any results generated by use of the Data, and user is entirely responsible for the results and any reliance on the results or the Data in general.
USER AGREES TO INDEMNIFY DOE/NLR/ALLIANCE AND ITS SUBSIDIARIES, AFFILIATES, OFFICERS, AGENTS, AND EMPLOYEES AGAINST ANY CLAIM OR DEMAND, INCLUDING REASONABLE ATTORNEYS' FEES, RELATED TO USER'S USE OF THE DATA. THE DATA ARE PROVIDED BY DOE/NLR/ALLIANCE "AS IS," AND ANY EXPRESS OR IMPLIED WARRANTIES, INCLUDING BUT NOT LIMITED TO THE IMPLIED WARRANTIES OF MERCHANTABILITY AND FITNESS FOR A PARTICULAR PURPOSE ARE DISCLAIMED. DOE/NLR/ALLIANCE ASSUME NO LEGAL LIABILITY OR RESPONSIBILITY FOR THE ACCURACY, COMPLETENESS, OR USEFULNESS OF THE DATA, OR REPRESENT THAT ITS USE WOULD NOT INFRINGE PRIVATELY OWNED RIGHTS. IN NO EVENT SHALL DOE/NLR/ALLIANCE BE LIABLE FOR ANY SPECIAL, INDIRECT OR CONSEQUENTIAL DAMAGES OR ANY DAMAGES WHATSOEVER, INCLUDING BUT NOT LIMITED TO CLAIMS ASSOCIATED WITH THE LOSS OF DATA OR PROFITS, THAT MAY RESULT FROM AN ACTION IN CONTRACT, NEGLIGENCE OR OTHER TORTIOUS CLAIM THAT ARISES OUT OF OR IN CONNECTION WITH THE ACCESS, USE OR PERFORMANCE OF THE DATA.

## LFP_LTO-Si
Function | Potential Failure | Effect | Severity | Potential cause of mechanisum of Failure | Occurrence | Detection Method | Detection Quality | RPN | Recommended Action
Fast charging 100% SOC charge in 15 minutes at Room temperature | Unintended Function (fire due to Li plating or SEI rupture under stress) | Fire and Smoke | 9 | Fast charging induces Li plating on LTO or Si surfaces and breaks weak SEI on Si due to volume expansion | 7 | Voltage relaxation, efficiency drop | 5 | 315 | Use current tapering, FEC/VC additives, soft binder design
Fast charging 100% SOC charge in 15 minutes at Room temperature | No Function (full capacity loss and severe degradation due to HF attack from LiPF6 decomposition) | Power loss and temperature rise | 10 | LiPF6 decomposes to PF5 + HF; HF corrodes Al and SEI, Irreversible Si degradation and loss of electronic contact after multiple cycles at a high rate | 7 | Sudden SoH drop, IR increase | 5 | 350 | Use additives (LiBOB, LiDFOB), HF scavengers, limit upper, Cycle at reduced C-rate; use Si-C composites; improve binder integrity
Fast charging 100% SOC charge in 15 minutes at Room temperature | Partial Function (decreased capacity and power loss) | Capacity fade and power loss | 6 | Partial lithium trapping in Si matrix and LFP cathode saturation dynamics | 6 | IR growth, capacity monitoring | 4 | 144 | Optimize electrode formulation; use capacity buffer
Fast charging 100% SOC charge in 15 minutes at Room temperature | Intermittent Function (erratic cell behavior due to unstable SEI) | Power loss and energy loss/Temperature rise | 5 | Unstable SEI reforms during cycling, causing inconsistent voltage and heat generation | 5 | Voltage irregularity tracking | 4 | 100 | Apply compliant binder; optimize formation cycles
Normal charge-discharge cycling | Unintended Function (gas generation and internal pressure rise) | Smoke or fire | 6 | Si expansion generates cracks and exposes fresh surfaces, initiating continuous electrolyte decomposition | 6 | Gas sensor, pressure rise | 4 | 144 | Encapsulate Si with carbon shell; dry-room electrolyte handling
Normal charge-discharge cycling | No Function (complete Li inventory loss) | Power loss and temperature rise | 6 | Loss of cyclable lithium due to repeated SEI reformation on Si during charge/discharge | 6 | Coulombic efficiency tracking | 4 | 144 | Pre-lithiate Si; limit depth of discharge
Normal charge-discharge cycling | Partial Function (capacity fade and impedance rise) | Capacity fade and power loss | 6 | SEI instability and cumulative impedance from both LTO and Si interface over aging | 6 | IR trend analysis | 4 | 144 | Use SEI-stabilizing additives; design low impedance electrodes
Normal charge-discharge cycling | Intermittent Function (voltage fluctuation due to contact loss) | Power loss and energy loss/Temperature rise | 5 | Contact loss at Si or LTO interface due to binder fatigue and electrolyte side reactions | 5 | Transient voltage monitoring | 4 | 100 | Use stress-relieving composite layers
Normal charge-discharge cycling at −10°C | Unintended Function (Li plating due to poor kinetics) | Smoke or fire | 9 | Low temperature suppresses Li+ mobility, leading to lithium plating and local hotspots | 5 | Overvoltage alarm, IR shift | 3 | 135 | Use low-temp optimized electrolyte; limit fast charging at low T
Normal charge–discharge cycling at –10 °C | No Function (complete Li inventory loss) | Power loss and temperature rise | 7 | Severe lithium plating on LTO or Si under low-temperature charge, leading to irreversible lithium loss and inactive lithium formation | 6 | Coulombic efficiency drop; post-cycle capacity loss analysis | 4 | 168 | Use moderate preheating (~10–15 °C); optimize low-temperature charge rate; electrolyte additives (e.g., FEC, ES); surface modification on Si to suppress Li plating
Normal charge-discharge cycling at −10°C | Partial Function (incomplete lithiation/delithiation at anode) | Capacity fade and power loss | 6 | Si shows poor lithiation dynamics below 0°C, creating stress gradients and poor utilization | 6 | Differential capacity analysis | 4 | 144 | Use nano-Si particles; increase ionic pathways
Normal charge-discharge cycling at −10°C | Intermittent Function (cycle instability from local overpotential) | Power loss and energy loss/Temperature rise | 5 | SEI thickening due to low-T impedance rise, local Li+ imbalance, and delayed charge transfer | 5 | Cycle-to-cycle voltage swing | 3 | 75 | Use protective SEI coatings; lower charging voltage
Rest condition at 100% SOC and 25°C for cycle-aged cells | No Function (resistance rise and lithium loss) | Accelerated aging leading to thermal instability | 5 | Chemical instability of SEI and electrolyte under prolonged high SOC rest leads to resistance rise | 5 | Voltage rest tracking | 3 | 75 | Avoid 100% SOC storage; thermal regulation
Rest condition at 100% SOC and 25°C for cycle-aged cells | Partial Function (SEI thickening and loss of active material) | Accelerated capacity fade and power loss | 6 | Side reactions at LTO or Si surface consume lithium and increase impedance | 6 | Self-discharge monitoring | 3 | 108 | Use stable electrolyte, apply protective coatings
Rest condition at 100% SOC and 25°C for cycle-aged cells | Intermittent Function (voltage drift and self-discharge) | Voltage drift, loss of reliability | 5 | Self-discharge via continuous parasitic reactions at active/inactive Si interfaces | 5 | Open circuit voltage deviation | 3 | 75 | Store at partial SOC; use voltage equalization
Rest condition at 100% SOC and 25°C for cycle-aged cells | Unintended Function (thermal runaway due to deep cycling stress) | Smoke or fire | 9 | Accumulated stress from repeated deep cycling leads to microcracking in Si particles and unstable SEI, resulting in exothermic reactions during rest | 5 | Voltage drift, surface temperature rise | 4 | 180 | Avoid prolonged rest at full SOC; design with buffer SOC window; reinforce SEI with additives (FEC, LiBOB); optimize Si content and morphology
Full discharge from 100% to 0% SOC at 25°C | Intermittent Function (voltage drift and self-discharge) | Power loss, unexpected SoC drop, energy loss | 5 | Incomplete delithiation of LTO or Si anode; formation of unstable SEI or inactive lithium zones during deep discharge; stress-induced SEI cracking | 5 | Voltage drift detection, BMS log review | 4 | 100 | Avoid deep discharge during early life; include sacrificial lithium reservoir; optimize SoC window; monitor BMS voltage anomalies
Full discharge from 100% to 0% SOC at 25°C | Unintended Function (thermal runaway due to deep cycling stress) | Smoke or fire | 8 | Extended discharge causes Li-Si de-lithiation instability, high overpotential, and exothermic failure | 6 | Thermal sensor alert, impedance | 4 | 192 | Control DOD range; apply thermal fuse
Full discharge from 100% to 0% SOC at 25°C | No Function (exhausted Li and isolation of active particles) | Power loss and temperature rise | 7 | Particle isolation and irreversible volume changes in Si disrupt percolation network | 6 | SoH monitoring, IR and capacity | 4 | 168 | Use Li reservoir design; include sacrificial lithium
Full discharge from 100% to 0% SOC at 25°C | Partial Function (reduced energy from degraded electrode contact) | Power loss and energy loss/Temperature rise | 6 | Mechanical fatigue in Si-LTO matrix weakens contact and lithium mobility | 5 | IR noise, capacity trend | 3 | 90 | Apply flexible electrode design; reduce binder fatigue
Normal charge-discharge cycling at elevated temperature (>40°C) | Unintended Function (gas evolution and electrolyte breakdown) | Smoke or fire | 9 | Heat accelerates electrolyte breakdown and SEI instability on Si-rich surfaces | 5 | Gas evolution detection | 4 | 180 | Replace EC with high temp-stable solvents
Normal charge-discharge cycling at elevated temperature (>40°C) | No Function (accelerated aging of LTO–Si interface) | Accelerated aging and SEI damage | 8 | Electrochemical stress at elevated temp breaks passivation layers at the interface | 6 | IR monitoring, impedance tracking | 4 | 192 | Apply high temp SEI stabilizer additives
Normal charge-discharge cycling at elevated temperature (>40°C) | Partial Function (decreased rate capability due to impedance growth) | Power loss and Energy loss | 6 | High temp SEI growth at LTO/Si interface increases IR drop and transport barrier | 5 | Charge rate loss tracking | 3 | 90 | Include electrolyte cooling; impedance matching
Normal charge-discharge cycling at elevated temperature (>40°C) | Intermittent Function (performance fluctuation due to thermal drift) | Power loss and energy loss/Temperature rise | 5 | SEI layer drift, resistance increase, and spatial stress variation due to thermal mismatch | 5 | Voltage and thermal mapping | 3 | 75 | Apply stack pressure control; monitor delta-T